How to change the Demand Limits with PecStar

Project:  AUO Crystal                                                                  Date: 2013/11/25

Note: Due to business development, since April 10th, 2017, Ceiec Electric Technology Inc. has been renamed to CET Electric Technology Inc., however, the products (including hardware and software) that were manufactured before this date may still involve old name or logo.

How to setup Alarm Limits with PecConfig

The alarm rule is a setpoint condition for a real-time source. The PecView is used to monitor the real-time vaules of the system, when an alarm rule is met, a real-time event will be generated and pushed up in the event window of HMI.

Follow the procedures to setup an alarm rule with PecConfig:

1. Click the  icon – PecAssistant from the Windows taskbar.

2. Click the PecConfig button to start the system configuration program.

3. Click the  icon in front of Station Setup and Station 1 on the left-hand pane to expand the tree. Then click on the Alarm Rule Setup folder. All alarm rules are displayed on the right-hand pane. Select the alarm rule you want to modify, and click the  icon from the tool bar.

4. The Alarm Condition Properties window appears. Set the High Limit, Low Limit, Action Delay(s) and Return Delay(s) as required.

Eval Mode: The Eval Mode specifies the criterion by which the source is evaluated. The options contain Less than and Greater than.

High Limit: When the Eval Mode is Greater than, the High Limit specifies what limit the source must exceed for an alarm to turn on. When the Eval Mode is Less than, the High Limit specifies what limit the source must exceed for an alarm to turn off.

Low Limit: When the Eval Mode is Greater than, the Low Limit specifies what limit the source must fall below for an alarm to turn off. When the Eval Mode is Less than, the Low Limit specifies what limit the source must fall below for an alarm to turn on.

The High Limit must be higher than or equal to the Low Limit.

Action Delay(s): When the Eval Mode is Greater than, the Action Delay(s) specifies the amount of time in seconds the source must exceed the High Limit for an alarm to turn on. When the Eval Mode is Lower than, the Action Delay(s) specifies the amount of time in seconds the source must fall below the Low Limit for an alarm to turn on.

Return Delay(s): When the Eval Mode is Greater than, the Return Delay(s) specifies the amount of time in seconds the source must fall below the Low Limit for an alarm to turn off. When the Eval Mode is Lower than, the Return Delay(s) specifies the amount of time in seconds the source must exceed the High Limit for an alarm to turn off.

Current Settings:

If TPC kW Demand is greater than 1650kW, a real-time event will be generated and pushed up.

5. Click the  icon in front of Demand Prediction Site on the left-hand pane to expand the tree. Right-click Demand Prediction Feeder and select Properties from the pop-up menus.

6. The Device Properties window appears. Click INF File>>.

8. The Edit Text File window appears. Change LimitValue highlighted in the red boxes if required and click OK.

8. Click the Save icon  from the tool bar. The System Config information box appears, click OK.

8. Restart the Front and PecDemandForecast from StartPrograms.

PecDemandForecast.exe

Front.exe

How to setup Alarm Limits with PecDraw

The user diagrams are created with PecDraw and displayed with PecView. In the “AUO Energy&Demand” diagram, the following objects have properties relative to the demand limit.

Follow the procedures to change the demand limit with PecDraw:

1. Click Windows Start  All Programs  PecStar V3.5  Client Workstation Module  PecDraw to start the program.

2. The Login window appears. Enter the correct user name and password. By default, User Name: ROOT, no password. Click OK.

3. Click the Open icon  from the tool bar. The Open window appears. Select the “AUO Energy&Demand.drw” file under the Graph folder and click Open.

4. The “AUO Energy&Demand.drw” file is open.

For the table(1):

Right-click on the object of TPC Sum kW Demand and select Properties… from the pop-up window.

5. The Shape Properties window appears. Navigate to the Normal Animation tab, click on the Define… button under Color Animation.

The Color Animation List window appears.

Select the first condition from the Animation Condition list and click Modify.

The Color Animation window appears. Enter the Min and Max value and click OK. If the source value is in the range of [Min, Max], the text object will be displayed in the color defined by Animation Result.

Select the second condition from the Animation Condition list and click Modify. Enter the Min and Max value and click OK.

Click Close to close the Color Animation List window.

Current Settings:

If kW Demand is in the range of [1500, 1700], the value will be displayed in Orange.

If kW Demand is in the range of [1700, 2000], the value will be displayed in Red.

Click on the Define… button under Blinker Animation.

The Blinker Animation window appears.

Select the condition from the Animation Condition list and click Modify.

The Blinker Animation window appears. Enter the Min and Max value and click OK. If the source value is in the range of [Min, Max], the text object will blink as an alarm to attract the attention of the operator.

Click Close to close the Blinker Animation window.

Click Ok and then close the Shape Properties window.

Current Settings:

If kW Demand is in the range of [1700, 2000], the value will blink.

For the bar (2):

6. Double-click on the object of 1000kW and the Shape Properties window appears.

Change the Text 1700kW to the new demand limit in the Text tab.

7. Double-click on the object of ####.# and the Shape Properties window appears. Navigate to the Normal Animation tab, click on the Define… button under Color Animation, Movement, and Blinker Animation with check box. Change the limit from pop-up window as step 5.

Change the properties for the objects of kW and the rectangle on the right in the same method.

For the dial (3):

8. Double-click on the dial object and the Shape Properties window appears. Navigate to the Special Properties tab, click on the Settings… button behind Coordinates.

The Dial window appears. Set the Start and End value of Filling 1, Filling 2, and Filling 3.

Click Ok to return to main window.

9. Click on the Save icon on the tool bar in PecDraw to save the diagram to local cache.

10.  Click File from the menu bar and select Upload Graph Repository.

The Confirm Upload dialog box appears. Click Ok to continue. Then the updated diagrams are saved to the database.

How to update the diagrams in PecView

1. Start PecView.

2. Right-click on the window and click Show/Hide Toolbar from the pop-up menus.

3. Click on the PecStar button at the left bottom of PecView and select Update GraphAll Graphs. If the diagrams are modified with PecDraw, the diagrams displayed in PecView will be updated.