How to do schedule control via PMC-53M’s DO with PecStar

Step 1.

Install the LightingCtrl driver - DrvLightingCtrl.dat & LightingCtrl.dat and the PMC-53M driver – DrvModbus.dat & PMC-53M.dat.

And copy the LightingCtrlSet.exe program to the \Common folder of PecStar iEMS.

Step 2. Configure with PecConfig

Take a PMC-53M V6.0 meter for example.

DO Configuration

- Start PMC Setup.

- Add a site and a device.

- Connect the device. Navigate to Setup  I/O Settings, and the I/O Settings window appears.  Set DO1 Pulse Width to 0.

.0

- Exit PMC Setup.

In PecConfig

- Start PecConfig.

- For PMC-53M meter:

- Add a site and a device for the PMC-53M matches with the communication parameters.

Then the default .snf file is imported. There are two DOs are included in the .snf file:

D16=DO1

D17=DO2

- Add a Digital Out data source. Right-click on the Digital Out Setup folder from the left-hand pane and select New…

- The Digital Out Properties dialog box appears.

- Enter a name in the Name box for identification.

- Set Site and Device as per the system to locate the meter.

- Set Code to 0.  For DO1, the code is 0.  For DO2, the code is 1.  The code is defined by the communication driver.

- Set Type to Open.

- Set Add in Bulk to 1.  The value specifies the number of pairs of the DO control data sources.  If the value is 1, a pair of DO control data source will be added, which type is set to Open and Close respectively.

Then click OK.

- The pair of DO control data source is listed at the bottom of the right-hand pane. Double-click on the last digital out data source and change its name for identification.  As below:

- Save the configuration to database.

- For LightingCtrl driver

- Add a virtual site. Enter Site Name, and set Driver Type to Lighting Control Site Driver. Leave other settings as default.

- Add a virtual device. Enter Device Name, and set Device Type to LightingCtrl. Leave other settings as default.

- Add an analog data point. Enter Name and set Code to 0. This data point is used for manual control mode.

Performing DO Control in Communications Station

- Start Communications Station.

- Right-click on the site and select Launch or Quit Online from the pop-up menu.  Leave all real sites offline, and then take the real PMC site online.

- Start PecConfig.

- Add the PMC-53M meter as he communication parameters.

- Then the default .snf file is imported. There are two DOs are included in the .snf file:

D16=DO1

D17=DO2

- Add a virtual site.