Siemens VSD Modbus Configuration in PecStar

How to configure a Siemens VSD according to its Modbus mapping with PecStar?

For example, the Modbus mapping of Siemens VSD#1 is as below:

| Items | Modbus Adress | Parameter | Format | Scale |
| --- | --- | --- | --- | --- |
| 1 | 40000 | Status Word 1 | UINT32* | Default=K0032 |
| 2 | 40001 | Status Word 2 | UINT32# | Default=K0033 |
| 3 | 40002-40003 | Speed | UINT32 |  |
| 4 | 40004 | Output Voltage | UINT16 |  |
| 5 | 40005 | Output Current | UINT16 |  |
| 6 | 40006 | Output Power | UINT16 |  |
| 7 | 40007 | Motor Torque | UINT16 |  |
| 8 | 40008 | DC Bus Voltage | UINT16 |  |

*The following illustrates the meanings of every bit of Status Word 1 register.

Bit0=Ready to power up

Bit1=Ready

Bit2=Run

Bit3=Fault

Bit4=OFF2

Bit5=OFF3

Bit6=Power-on inhibit

Bit7=Alarm

Bit8=Setpoint-actual value deviation

Bit9=PZD control requested

Bit10=Comparison frequency reached

Bit11=Undervoltage

Bit12=Main contractor energized

Bit13=RFG active

Bit14=Clockwise rotating field

Bit15=KIP/FLN active

# The following illustrates the meanings of every bit of Status Word 2 register.

Bit16=Restart-on-the-fly active

Bit17=Synchronism has been reached

Bit18=Overspeed

Bit19=External fault 1

Bit20=External fault 2

Bit21=External alarm

Bit22=Alarm i2t drive converter

Bit23=Fault, converter overtemperature

Bit24= Alarm, converter overtemperature

Bit25=Alarm, motor overtemperature

Bit26= Fault, motor overtemperature

Bit27=Reserve

Bit28= Fault, motor stalled/locked

Bit29=Bypass contractor energized

Bit30= Alarm sync. error

Bit31= Pre-charging active

To read the parameters, please make configurations following the steps:

- Step I Start PecConfig

- Step II Add a site

Right-click on the Communication Setup folder from the left-hand pane, select New…, and the Site Node Properties window appears.  Set the Driver Type to MODBUS Protocol Master Site Driver.  Set the Serial Port parameters to match the port and device.

Add a device. Click + to expand the Communication Setup folder. Right-click on the Site I, select New…, and the Device Node Properties window appears.  Set the Type to ModbusMeter.

Right-click the Device I and select Properties.  Click Appendix>> from the Device Properties box and you will see the following box.

- Step III Edit Modbus Block properties

Click Add Data Block>> from the Appendix setup for MODBUS Protocol Master Site Driver’s configuration file window, and the Block Edit dialog box appears.

Data Type: Set to Analog In for analog measurements and set to Digital In for status measurements.

Data Format: Set to NUM_U32INT for unsigned 32-bit integer.

NUM_U16INT: unsigned 16-bit integer.

NUM_S16INT: signed 16-bit integer.

NUM_U32INT: unsigned 32-bit integer.

NUM_S32INT: signed 32-bit integer.

NUM_U32MFP: unsigned 32-bit float.

NUM_S32MFP: signed 32-bit float.

OpCode: Enter 03 (the function code 03 is read registers)

Start Address: Enter 0.  Set Start Address according to the device’s Modbus mapping.

Source No.: Enter 1.  It’s the number of parameters with the same data format.

Start Code: Enter 0.  It’s same with the code number of every parameters in PecConfig which has marked by red rectangle in the following figure.

Click OK from the Block Edit window. The Modbus block added is listed in the Data Block List area.

Click Add a Block>> to add other Modbus block.

After all Modbus blocks are added, click OK from the Appendix setup for MODBUS Master Site’s configuration file window.

Click Ok from the Device Node Properties window.

- Step IV Import Device SNF

Import SNF file by right click on the Device I and select Import SNF File.

Save to database. Click Save from the tool bar. Exit PecConfig.

Start Front. Check the readings with the device.

Note: Select a Type from the drop-down list. No need to match the Type to your device.

- Appendix A SNF File of Siemens VSD#1

A0=Speed

A1=Output voltage

A2=Output amps

A3=Output power

A4=Motor torque

A5=DC Bus Volt

D0=Ready to power-up

D1=Ready

D2=Run

D3=Fault

D4=OFF2

D5=OFF3

D6=Power-on inhibit

D7=Alarm

D8=Setpoint-actual value deviation

D9=PZD control requested

D10=Comparison frequency reached

D11=Undervoltage

D12=Main contactor energized

D13=RFG active

D14=Clockwise rotating field

D15=KIP/FLN active

D16=Restart-on-the-fly active

D17=Synchronism has been reached

D18=Overspeed

D19=External fault 1

D20=External fault 2

D21=External alarm

D22=Alarm i2t drive converter

D23=Fault, converter overtemperature

D24=Alarm, converter overtemperature

D25=Alarm, motor overtemperature

D26=Fault, motor overtemperature

D27=Reserve

D28=Fault, motor stalled/locked

D29=Bypass contactor energized

D30=Alarm sync. error

D31=Pre-charging active